[image: image1.png]Pvok dv'= ®



                 PROK DEVICES PRIVATE LIMITED

B-80, 2nd & 3rd Floor, KSSIDC Industrial estate, 4th Main Road,

 6th Block, Rajaji Nagar, Bengaluru -560010

Ph no: 080-41480777, 080-41157700, Email: enquiry@prokdvs.com,

www.prokdvs.com, www.prokdvs.in
AC VOLTAGE RELAY

LVM SERIES 
Introduction

Prok dvs make AC Digital Microcontroller Based Definite-Time Under Voltage (UV) and Over Voltage (OV)/ Line Voltage Monitor (LVM) is a microcontroller based voltage monitoring and supervision  relay  for poly-phase system. It can monitor both under voltage (UV) and over voltage (OV) conditions in the system. Both under voltage (UV) & over voltage (OV) conditions are associated with definite time tripping characteristics. It has wide setting range of operating time on the occurrence of fault condition. 

DIGITAL MICROCONTROLLER BASED DEFINITE TIME UNDER VOLTAGE (UV) AND OVER VOLTAGE RELAY/ LINE VOLTAGE MONITOR(LVM) provides wide range of time delay for healthy resumption of the operating voltage.  
FEATURES

· Site selectable system voltage
· Continuous display of measured voltage parameter
· 6 character 2 line LCD display with back-lit
· Accurate reading for balanced and unbalanced load. 
· Wide range of auxiliary input for both AC  & DC
· Independent contacts for Under & Over voltage
· Self reset & site selectable reset gap
· Built in fixed instantaneous Under & Over voltage  
· User friendly setting modes using keypads
· Low power consumption
· Tropicalized design using microcontroller & ideal for industrial environment
APPLICATION

· Monitoring & Supervision of Under and Over Voltage in power generating plants & distribution system
· To protect Generator & AMF switchboards
· For protection of synchronous & induction motors
· For transformer feeder panel
· Protection for capacitor control panels
WORKING PRINCIPLE

All the line voltages are monitored and sensed simultaneously using three independent scale down potential transducer. This low level ac signal is subjected to signal conditioning, which includes surge suppressors and harmonic filter. The filtered signal is fed to the ADC of the industrial grade microprocessor. When the sensing voltage exceeds the user set value for under or over voltage, the relay given an output signal in the form of relay changeover for tripping/alarming.
Setting Procedure for AC Voltage Relay (LVM Series) 3P 4W
Step1:  Connect the suitable auxiliary supply in the range of 85 -275V AC/DC voltage  
 to the P (+) & N (-) Terminals Refer wiring diagram LVM 01/02/03 2C/O
 Display shows for a while
Then display shows (if sensing 3ph voltages                   [image: image2.jpg]



Are not given)

[image: image3.jpg]


 

Step2:   Press [image: image4.jpg]


key to enter the setting mode
Setting mode consists of Mode 0 to mode 6 depending upon the models (LVM11, LVM02, LVM03) Modes will vary
In mode 0 - Display Shows Rated voltage (Un) selection
Select suitable rated voltage            
[image: image5.jpg]


    1) 380V L-L corresponds to 220V P-N 

                                                          2) 400V L-L corresponds to 230V P-N

                                                          3) 415V L-L corresponds to 240V P-N

                                                          4) 433V L –L corresponds to 250VP-N
After selecting the Rated Voltage Un, press[image: image6.jpg]


 key to save the value

Display shows - Set Under voltage [70-99.0%] – Mode 1. 
[image: image7.jpg]



In mode 1- Select the suitable under voltage in the range of 70% to 99% of selected
 Un (220 to 250) P-N by using [image: image8.jpg]


 or[image: image9.jpg]


key
After selecting the suitable % of Under voltage of Un, Press[image: image10.jpg]


key to save the value. Display Shows – Set UV Trip time [0 -30 secs] DEFT selection – Mode 2
[image: image11.jpg]



In mode 2- Select the suitable UV Trip Time in the range of 00.0- 30.0S in steps of 0.1S by using  [image: image12.jpg]


 or[image: image13.jpg]


key
 After selecting the UV Trip Time press[image: image14.jpg]


key to save the value.

Display Shows- Set Over Voltage [101-120%] - mode 3

[image: image15.jpg]



In mode 3- Select the suitable over voltage in the range of 101% to 120% of Selected Un (220 to 250) P-N by using  [image: image16.jpg]


 or[image: image17.jpg]


key
After selecting the suitable % of over voltage of Un, Press[image: image18.jpg]


key to save the value. Display Shows – Set OV Trip time [0 -30 secs] DEFT selection – Mode 4
[image: image19.jpg]



In mode 4- Select the suitable OV Trip Time in the range of 00.0- 30.0S in steps of 0.1S
 After selecting the OV Trip Time, press[image: image20.jpg]


key to save the value.

Display Shows – Set ON Delay [0 -30 secs]  UV&OV DEFT selection – Mode 5
[image: image21.jpg]



In mode 5- Select the suitable ON Delay in the range of 00.0- 30.0S in steps of 0.1S by using  [image: image22.jpg]


 or[image: image23.jpg]


key
 After selecting the ON Delay, press[image: image24.jpg]


key to save the value.

Note: ON Delay is common for both UV & OV settings

          ON Delay is the Delay from fault to healthy state
Display Shows – Set Reset Gap [1% -5%] UV&OV selection – Mode 6
[image: image25.jpg]



In mode 6- Select the suitable Reset gap in the range of 1%- 5% of Un in steps of 1% by using  [image: image26.jpg]


 or[image: image27.jpg]


key
 After selecting the Reset Gap, press SET key to save the value.

Note: % Reset gap is common for both UV & OV settings

          % Reset gap (UN) is the voltage above or below the set UV/OV corresponding to reset from fault to healthy state.
If the sensing input voltages are given to R, Y, B, N Terminals refer wiring diagram

Display shows

NOTE: During setting mode, If none of the key was pressed within 15 sec display returns to normal working condition retaining the previous settings.
MODELS:1) LVM11- Both Under & Over Voltage -3P4W

                 2) LVM02- Only Under Voltage -3P4W
                 3) LVM11- Only Over Voltage - 3P4W

[image: image28.png]NS OF DIGITAL
IME UNDER
RELAY / LINE

E k-1 5,
o A
FRONT VIEW. zlnrs-u—/_zl._
SIDE VIEW
——
3|





[image: image29.png]ROLLER BASED
D OVER
ONITOR (LVM)

— o come
H
w s 3]s
¥
wvo | : : M
N
B i d — # |» [®5-27vaATC
ovit e —{ & (| N [aux suppLy
e Ty et

NOTE: FOR SHUNT RELEASE CONNECT C & NIO CONTACTS.
FOR UV RELEASE OR CONTACTOR COIL CONNECT C & NIC CONTACTS
ARE SHOWING IN HEALTHY CONDITION





[image: image30.png]DIGITAL MICROCONTROLLER BASED DEFINITE-TIME UNDER
VOLTAGE (V) AND OVER VOLTAGE (QV) RELAY / LINE

VOLTAGE MONITOR (LVM) iccc pevice cope-az. s

v B3
w13 p
s bs
o |18 ¢
o218 g3
=3 q3

o3 T3 b3l
== =3 E3H
sa_ )3 w3 =3
e L e — e |~
=Y =S BB






Wiring Diagram:
[image: image31.jpg]WIRING DIAGRAM FOR LVM 11 2C/O

LOAD

SOURCE

zZwWw <D

y [ —

"NYNEnYy

"TOVALM

RATED VOLTAGE FOR
HUNT TRIP COIL / UVR
ROM LOAD SIDE





Technical Specification
[image: image32.png]Aux voltage

System voltage Un

Over voltage setting range
Over voltage trip time
Under voltage setting range
Under voltage trip time.
Reset gap

On time delay
Default high set setting
With instantaneous trip

Contacts.

Indications.

Model dimension

Cut out dimension

Model

3Phase 4 Wire
8510275V AC/DC
'220V230V/240V/250VAC site selectable
101% to 120% in steps of 1% site selectable
0-30sec in steps of O.1sec

70%t0 99% in steps 1% Site selectable
0-30sec in steps of O.1sec

1%t0 5% o f Un in steps of 1%
0-30sec in steps of 1sec

Fixed UV high set <70% of Un

Fixed OV high set >120% of Un

Independent contact for UV/OV.
1/00r 2¢/0, 6A-230VAC

Display of the Magnitude and nature of
fault by LCD an d LED indications for relay.
trip

144x144x120mm [Hx W x D]
1mmtolerance.
157 mmx137mm

LVM11-Both UV&OV
LVMO2-UV only
LVMO3-OVonly

3 Phase 3 Wire
85t0275VAC/OC
110V/380v/400v/415V/433VACsite selectable
101% to 120% insteps of 1% site selectable
0-30sec in steps o f O.1sec

70%t0 997% n steps 1% ite selectable
0-30ec in steps of 0.1sec

1%t0 5% 0 FUn in steps of 1%

0-30sec in steps of 1sec

Fixed UV high set <70% of Un
Fixed OV high set >120% of Un

Independent contact for UV/OV.
1/00r 2¢/0, 6A-230VAC

Display of the Magnitude and nature of
fault by LCD an d LED indications for relay.
trip

144x144x120mm [Hx W x D]
1mmtolerance.

157 mmx137mm
LVM11A-Both UVEOV
LVMO2A-Uvonly
LVMO3A-OVonly
































   Rn-220V      Yn- 220V


   Bn-220V     3P4W /220









































